## Sheet1 (hidden)
| Air Temp (F) | Air Temp (K) | Home Temp (K) | Difference
January | 42 | 278.7056 | 294.261 | -15.5554 | COLD
February | 46 | 280.9278 | 294.261 | -13.3332 | COLD
March | 55 | 285.9278 | 294.261 | -8.3332 | COLD
April | 66 | 292.0389 | 294.261 | -2.2221 | COLD
May | 76 | 297.5944 | 294.261 | 3.3334 | HOT
June | 84 | 302.0389 | 294.261 | 7.7779 | HOT
July | 88 | 304.2611 | 294.261 | 10.0001 | HOT
August | 86 | 303.15 | 294.261 | 8.889 | HOT
September | 79 | 299.2611 | 294.261 | 5.0001 | HOT
October | 68 | 293.15 | 294.261 | -1.111 | COLD
November | 57 | 287.0389 | 294.261 | -7.2221 | COLD
December | 46 | 280.9278 | 294.261 | -13.3332 | COLD

## h_OUT
| Wind Speed (m/s) | Home Temp (F) | Home Temp (K) | Air Temp (F) | Air Temp (K) | Density (kg/m3) | Cp (KJ/kgK) | Dynamic Visocity (Ns/m2) | Kinematic Viscosity (m2/s) | Thermal Conductivity (W/mK) | Thermal Diffusivity (m2/s) | Prandlts Number | Reynolds Number | Condition | Nusselt Number | Heat Transfer Coefficient Outside (W/m2K)
January | 6 | 70 | 294.261 | 42 | 278.7056 | 1.2608 | 1.0066 | 1.7395e-05 | 1.3995e-05 | 0.024596 | 1.9689e-05 | 0.71254 | 964644.3936 | Turbulent | 1248.0078 | 13.6429
February | 6 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888
March | 7 | 70 | 294.261 | 55 | 285.9278 | 1.2271 | 1.0067 | 1.7756e-05 | 1.4638e-05 | 0.025174 | 2.0642e-05 | 0.71066 | 1075998.1069 | Turbulent | 1431.7755 | 16.0195
April | 6 | 70 | 294.261 | 66 | 292.0389 | 1.1985 | 1.0068 | 1.8062e-05 | 1.5181e-05 | 0.025663 | 2.1449e-05 | 0.70907 | 889242.4715 | Turbulent | 1118.4771 | 12.7572
May | 5 | 70 | 294.261 | 76 | 297.5944 | 1.1726 | 1.007 | 1.834e-05 | 1.5676e-05 | 0.026108 | 2.2182e-05 | 0.70763 | 717661.8895 | Turbulent | 819.2468 | 9.506
June | 5 | 70 | 294.261 | 84 | 302.0389 | 1.1546 | 1.0071 | 1.8556e-05 | 1.6095e-05 | 0.026451 | 2.2802e-05 | 0.70671 | 698969.9633 | Turbulent | 785.5792 | 9.2352
July | 5 | 70 | 294.261 | 88 | 304.2611 | 1.1472 | 1.0072 | 1.8661e-05 | 1.6319e-05 | 0.026615 | 2.3131e-05 | 0.7064 | 689394.5114 | Turbulent | 768.3306 | 9.0886
August | 5 | 70 | 294.261 | 86 | 303.15 | 1.1509 | 1.0071 | 1.8609e-05 | 1.6207e-05 | 0.026533 | 2.2966e-05 | 0.70656 | 694149.2168 | Turbulent | 776.9011 | 9.1616
September | 5 | 70 | 294.261 | 79 | 299.2611 | 1.1648 | 1.007 | 1.8423e-05 | 1.5824e-05 | 0.026241 | 2.2402e-05 | 0.70719 | 710934.6667 | Turbulent | 807.1067 | 9.413
October | 5 | 70 | 294.261 | 68 | 293.15 | 1.1934 | 1.0069 | 1.8117e-05 | 1.528e-05 | 0.025752 | 2.1596e-05 | 0.70878 | 736239.6804 | Turbulent | 852.6655 | 9.759
November | 6 | 70 | 294.261 | 57 | 287.0389 | 1.2219 | 1.0067 | 1.7812e-05 | 1.4736e-05 | 0.025263 | 2.0789e-05 | 0.71037 | 916095.1125 | Turbulent | 1164.8345 | 13.0788
December | 6 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888
|  |  |  | Table A4 Data | 250 | 1.3947 | 1.006 | 1.596e-05 | 1.144e-05 | 0.0223 | 1.59e-05 | 0.72
[5 empty] | 300 | 1.1614 | 1.007 | 1.846e-05 | 1.589e-05 | 0.0263 | 2.25e-05 | 0.707
[5 empty] | 350 | 0.995 | 1.009 | 2.082e-05 | 2.092e-05 | 0.03 | 2.99e-05 | 0.7

## h_IN
| Home Temp (F) | Home Temp (K) | Air Temp (F) | Air Temp (K) | Surface Temp (K) | Density (kg/m3) | Cp (KJ/kgK) | Dynamic Visocity (Ns/m2) | Kinematic Viscosity (m2/s) | Thermal Conductivity (W/mK) | Thermal Diffusivity (m2/s) | Prandlts Number | Rayleigh Number | Nusselt Number | Heat Transfer Coefficient Inside (W/m2K)
January | 70 | 294.261 | 42 | 278.7056 | 221.8134 | 1.2608 | 1.0066 | 1.7395e-05 | 1.3995e-05 | 0.024596 | 1.9689e-05 | 0.71254 | 113742319482.3057 | 23.7779 | 0.25993
February | 70 | 294.261 | 46 | 280.9278 | 231.9049 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 93293150436.2291 | 23.0301 | 0.25358
March | 70 | 294.261 | 55 | 285.9278 | 254.718 | 1.2271 | 1.0067 | 1.7756e-05 | 1.4638e-05 | 0.025174 | 2.0642e-05 | 0.71066 | 53221449321.7474 | 21.043 | 0.23544
April | 70 | 294.261 | 66 | 292.0389 | 283.4184 | 1.1985 | 1.0068 | 1.8062e-05 | 1.5181e-05 | 0.025663 | 2.1449e-05 | 0.70907 | 12868440186.5322 | 16.779 | 0.19138
May | 70 | 294.261 | 76 | 297.5944 | 310.3263 | 1.1726 | 1.007 | 1.834e-05 | 1.5676e-05 | 0.026108 | 2.2182e-05 | 0.70763 | 17060474738.3718 | 17.5429 | 0.20356
June | 70 | 294.261 | 84 | 302.0389 | 330.9626 | 1.1546 | 1.0071 | 1.8556e-05 | 1.6095e-05 | 0.026451 | 2.2802e-05 | 0.70671 | 35710049297.6095 | 19.7303 | 0.23195
July | 70 | 294.261 | 88 | 304.2611 | 341.1304 | 1.1472 | 1.0072 | 1.8661e-05 | 1.6319e-05 | 0.026615 | 2.3131e-05 | 0.7064 | 43629376658.5427 | 20.3712 | 0.24097
August | 70 | 294.261 | 86 | 303.15 | 336.0565 | 1.1509 | 1.0071 | 1.8609e-05 | 1.6207e-05 | 0.026533 | 2.2966e-05 | 0.70656 | 39772670607.1631 | 20.0724 | 0.2367
September | 70 | 294.261 | 79 | 299.2611 | 318.1234 | 1.1648 | 1.007 | 1.8423e-05 | 1.5824e-05 | 0.026241 | 2.2402e-05 | 0.70719 | 24540012127.2773 | 18.5859 | 0.21676
October | 70 | 294.261 | 68 | 293.15 | 288.7831 | 1.1934 | 1.0069 | 1.8117e-05 | 1.528e-05 | 0.025752 | 2.1596e-05 | 0.70878 | 6356488180.4687 | 15.009 | 0.17178
November | 70 | 294.261 | 57 | 287.0389 | 259.9511 | 1.2219 | 1.0067 | 1.7812e-05 | 1.4736e-05 | 0.025263 | 2.0789e-05 | 0.71037 | 45114598475.5558 | 20.4928 | 0.23009
December | 70 | 294.261 | 46 | 280.9278 | 231.9049 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 93293150436.2291 | 23.0301 | 0.25358
|  |  | Table A4 Data | 250 |  | 1.3947 | 1.006 | 1.596e-05 | 1.144e-05 | 0.0223 | 1.59e-05 | 0.72
|  |  |  | 300 |  | 1.1614 | 1.007 | 1.846e-05 | 1.589e-05 | 0.0263 | 2.25e-05 | 0.707
|  |  |  | 350 |  | 0.995 | 1.009 | 2.082e-05 | 2.092e-05 | 0.03 | 2.99e-05 | 0.7

## Iteration
January |  |  |  | T_air | 278.7056 | July |  |  |  | T_air | 304.2611
h_IN | q | R | qR = ∆T | T_inf | T_surf | h_IN | q | R | qR = ∆T | T_inf | T_surf
10 | 2413.7014 | 0.004 | 9.6548 | 294.26 | 284.6052 | 10 | 1496.1761 | 0.004 | 5.9847 | 294.26 | 300.2447
0.18495 | 352.9401 | 0.21627 | 76.3319 | 294.26 | 217.9281 | 0.17566 | 215.8524 | 0.22772 | 49.1535 | 294.26 | 343.4135
0.26245 | 474.5262 | 0.15241 | 72.3233 | 294.26 | 221.9367 | 0.24267 | 284.0097 | 0.16483 | 46.8138 | 294.26 | 341.0738
0.25985 | 470.6621 | 0.15393 | 72.4506 | 294.26 | 221.8094 | 0.24093 | 282.3182 | 0.16602 | 46.8718 | 294.26 | 341.1318
0.25994 | 470.7872 | 0.15388 | 72.4465 | 294.26 | 221.8135 | 0.24097 | 282.3611 | 0.16599 | 46.8703 | 294.26 | 341.1303
0.25993 | 470.7831 | 0.15389 | 72.4466 | 294.26 | 221.8134 | 0.24097 | 282.36 | 0.166 | 46.8704 | 294.26 | 341.1304
0.25993 | 470.7832 | 0.15389 | 72.4466 | 294.26 | 221.8134 | 0.24097 | 282.36 | 0.166 | 46.8704 | 294.26 | 341.1304
February |  |  |  | T_air | 280.9278 | August |  |  |  | T_air | 303.15
h_IN | q | R | qR = ∆T | T_inf | T_surf | h_IN | q | R | qR = ∆T | T_inf | T_surf
10 | 2067.0981 | 0.004 | 8.2684 | 294.26 | 285.9916 | 10 | 1331.0899 | 0.004 | 5.3244 | 294.26 | 299.5844
0.18086 | 296.6539 | 0.22117 | 65.6109 | 294.26 | 228.6491 | 0.17233 | 188.734 | 0.23211 | 43.8065 | 294.26 | 338.0665
0.25592 | 398.3084 | 0.1563 | 62.2559 | 294.26 | 232.0041 | 0.23837 | 248.7774 | 0.16781 | 41.747 | 294.26 | 336.007
0.25351 | 395.2051 | 0.15779 | 62.3582 | 294.26 | 231.9018 | 0.23666 | 247.2985 | 0.16902 | 41.7977 | 294.26 | 336.0577
0.25358 | 395.3016 | 0.15774 | 62.355 | 294.26 | 231.905 | 0.23671 | 247.3358 | 0.16899 | 41.7964 | 294.26 | 336.0564
0.25358 | 395.2986 | 0.15774 | 62.3551 | 294.26 | 231.9049 | 0.2367 | 247.3348 | 0.16899 | 41.7965 | 294.26 | 336.0565
0.25358 | 395.2987 | 0.15774 | 62.3551 | 294.26 | 231.9049 | 0.2367 | 247.3349 | 0.16899 | 41.7965 | 294.26 | 336.0565
March |  |  |  | T_air | 285.9278 | September |  |  |  | T_air | 299.2611
h_IN | q | R | qR = ∆T | T_inf | T_surf | h_IN | q | R | qR = ∆T | T_inf | T_surf
10 | 1307.4907 | 0.004 | 5.23 | 294.26 | 289.03 | 10 | 750.9467 | 0.004 | 3.0038 | 294.26 | 297.2638
0.16908 | 175.0855 | 0.23658 | 41.421 | 294.26 | 252.839 | 0.1571 | 97.9409 | 0.25461 | 24.9367 | 294.26 | 319.1967
0.23733 | 234.308 | 0.16854 | 39.4911 | 294.26 | 254.7689 | 0.21822 | 130.0518 | 0.1833 | 23.8382 | 294.26 | 318.0982
0.23539 | 232.7012 | 0.16993 | 39.5434 | 294.26 | 254.7166 | 0.21673 | 129.2983 | 0.18457 | 23.864 | 294.26 | 318.124
0.23544 | 232.7455 | 0.16989 | 39.542 | 294.26 | 254.718 | 0.21676 | 129.3163 | 0.18454 | 23.8634 | 294.26 | 318.1234
0.23544 | 232.7443 | 0.16989 | 39.542 | 294.26 | 254.718 | 0.21676 | 129.3159 | 0.18454 | 23.8634 | 294.26 | 318.1234
April |  |  |  | T_air | 292.0389 | October |  |  |  | T_air | 293.15
h_IN | q | R | qR = ∆T | T_inf | T_surf | h_IN | q | R | qR = ∆T | T_inf | T_surf
10 | 342.8889 | 0.004 | 1.3716 | 294.26 | 292.8884 | 10 | 167.2902 | 0.004 | 0.66916 | 294.26 | 293.5908
0.138 | 38.8913 | 0.28985 | 11.2726 | 294.26 | 282.9874 | 0.12367 | 17.5613 | 0.32345 | 5.6802 | 294.26 | 288.5798
0.19259 | 52.1535 | 0.2077 | 10.8322 | 294.26 | 283.4278 | 0.17278 | 23.6402 | 0.23151 | 5.4729 | 294.26 | 288.7871
0.19135 | 51.8647 | 0.20904 | 10.8418 | 294.26 | 283.4182 | 0.17176 | 23.5187 | 0.23288 | 5.477 | 294.26 | 288.783
0.19138 | 51.8711 | 0.20901 | 10.8416 | 294.26 | 283.4184 | 0.17178 | 23.5211 | 0.23285 | 5.4769 | 294.26 | 288.7831
0.19138 | 51.871 | 0.20901 | 10.8416 | 294.26 | 283.4184 | 0.17178 | 23.5211 | 0.23285 | 5.4769 | 294.26 | 288.7831
May |  |  |  | T_air | 297.5944 | November |  |  |  | T_air | 287.0389
h_IN | q | R | qR = ∆T | T_inf | T_surf | h_IN | q | R | qR = ∆T | T_inf | T_surf
10 | 501.1969 | 0.004 | 2.0048 | 294.26 | 296.2648 | 10 | 1116.9564 | 0.004 | 4.4678 | 294.26 | 289.7922
0.14723 | 61.6638 | 0.27169 | 16.7532 | 294.26 | 311.0132 | 0.16512 | 148.3278 | 0.24225 | 35.9321 | 294.26 | 258.3279
0.20488 | 82.2116 | 0.19524 | 16.0509 | 294.26 | 310.3109 | 0.23191 | 198.6643 | 0.17248 | 34.2656 | 294.26 | 259.9944
0.20353 | 81.7495 | 0.19654 | 16.0667 | 294.26 | 310.3267 | 0.23004 | 197.3213 | 0.17388 | 34.31 | 294.26 | 259.95
0.20356 | 81.7601 | 0.19651 | 16.0663 | 294.26 | 310.3263 | 0.2301 | 197.3578 | 0.17384 | 34.3088 | 294.26 | 259.9512
0.20356 | 81.7599 | 0.19651 | 16.0663 | 294.26 | 310.3263 | 0.23009 | 197.3568 | 0.17384 | 34.3089 | 294.26 | 259.9511
[6 empty] | 0.23009 | 197.3568 | 0.17384 | 34.3089 | 294.26 | 259.9511
June |  |  |  | T_air | 302.0389 | December |  |  |  | T_air | 280.9278
h_IN | q | R | qR = ∆T | T_inf | T_surf | h_IN | q | R | qR = ∆T | T_inf | T_surf
10 | 1165.714 | 0.004 | 4.6629 | 294.26 | 298.9229 | 10 | 2067.0981 | 0.004 | 8.2684 | 294.26 | 285.9916
0.16866 | 162.0897 | 0.23716 | 38.4414 | 294.26 | 332.7014 | 0.18086 | 296.6539 | 0.22117 | 65.6109 | 294.26 | 228.6491
0.23357 | 214.0649 | 0.17126 | 36.6602 | 294.26 | 330.9202 | 0.25592 | 398.3084 | 0.1563 | 62.2559 | 294.26 | 232.0041
0.23191 | 212.7971 | 0.17248 | 36.7036 | 294.26 | 330.9636 | 0.25351 | 395.2051 | 0.15779 | 62.3582 | 294.26 | 231.9018
0.23195 | 212.8286 | 0.17245 | 36.7025 | 294.26 | 330.9625 | 0.25358 | 395.3016 | 0.15774 | 62.355 | 294.26 | 231.905
0.23195 | 212.8279 | 0.17245 | 36.7026 | 294.26 | 330.9626 | 0.25358 | 395.2986 | 0.15774 | 62.3551 | 294.26 | 231.9049
0.23195 | 212.8279 | 0.17245 | 36.7026 | 294.26 | 330.9626 | 0.25358 | 395.2987 | 0.15774 | 62.3551 | 294.26 | 231.9049

## Main_Model
h_IN | 0.25358 | W/m2K
h_OUT | 13.4888 | W/m2K
T_air | 280.9278 | K
[6 empty] | 0.085729 |  | 0.02623 |  | 0.0016116
|  |  | 0.14084 | 0.012841 | [7 empty] | 280.9278 | K
[6 empty] | 10.5161 |  | 0.05018 |  | 0.19769
|  |  | 0.15774 | 0.02881 |  | 0.0029654
|  |  | 0.12721 | 0.02977 |  | 0.0023915
294.26 | K |  | 0.17925 | 0.0301 |  | 0.0033698 |  | 280.9278 | K
|  |  | 0.14084 | 0.03033 |  | 0.0026477
|  |  | 0.21909 | 0.03412 |  | 0.0041186
[6 empty] | 0.045855 |  | 0.0355
|  |  | 0.11267 | 0.012841 | [5 empty] | 291 | K
[6 empty] | 0.11267 |  | 0.04151
|  |  | 0.15368 | 0.11239 |  | 280.9278 | K
0.18952
0.15937
294.26 | K |  | 0.21272 | 280.9278 | K
0.17382
0.25732
|  |  | 0.12551 | 0.053255 |  | 291 | K
|  |  | 0.26607 | 280.9278 | K
294.26 | K |  | 0.038623 | 280.9278 | K
|  |  | 0.17877 | 291 | K
294.26 | K |  | 0.033727 | 280.9278 | K |  | 395.2987 | W
294.26 | K |  | 0.17877 | 291 | K |  | 18.2359 | W

## Main_Plot
| Wind Speed (m/s) | Soil Temp (K) | Home Temp (F) | Home Temp (K) | Air Temp (F) | Air Temp (K) | Density (kg/m3) | Cp (KJ/kgK) | Dynamic Visocity (Ns/m2) | Kinematic Viscosity (m2/s) | Thermal Conductivity (W/mK) | Thermal Diffusivity (m2/s) | Prandlts Number | Reynolds Number | Rayleigh Number | Nusselt Number | Heat Transfer Coefficient Outside (W/m2K) | Month | h_IN (W/m2K) | h_OUT (W/m2K) | R_Home (K/W) | R_Soil (K/W) | q_Home (W) | q_Soil (W) | q_5Human,2Cat (W) | q_Required (W)
January | 6 | 291.15 | 70 | 294.261 | 42 | 278.7056 | 1.2608 | 1.0066 | 1.7395e-05 | 1.3995e-05 | 0.024596 | 1.9689e-05 | 0.71254 | 964644.3936 | Turbulent | 1248.0078 | 13.6429 | COLD | 0.25993 | 13.6429 | 0.03304 | 0.1752 | 470.7832 | 18.6068 | 22.5 | 466.89
February | 6 | 291.15 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888 | COLD | 0.25358 | 13.4888 | 0.033727 | 0.17877 | 395.2987 | 18.2359 | 22.5 | 391.0346
March | 7 | 291.15 | 70 | 294.261 | 55 | 285.9278 | 1.2271 | 1.0067 | 1.7756e-05 | 1.4638e-05 | 0.025174 | 2.0642e-05 | 0.71066 | 1075998.1069 | Turbulent | 1431.7755 | 16.0195 | COLD | 0.23544 | 16.0195 | 0.0358 | 0.19 | 232.7443 | 17.1582 | 22.5 | 227.4025
April | 6 | 291.15 | 70 | 294.261 | 66 | 292.0389 | 1.1985 | 1.0068 | 1.8062e-05 | 1.5181e-05 | 0.025663 | 2.1449e-05 | 0.70907 | 889242.4715 | Turbulent | 1118.4771 | 12.7572 | COLD | 0.19138 | 12.7572 | 0.04282 | 0.22612 | 51.871 | 14.4174 | 22.5 | 43.7884
May | 5 | 291.15 | 70 | 294.261 | 76 | 297.5944 | 1.1726 | 1.007 | 1.834e-05 | 1.5676e-05 | 0.026108 | 2.2182e-05 | 0.70763 | 717661.8895 | Turbulent | 819.2468 | 9.506 | HOT | 0.20356 | 9.506 | 0.040783 | 0.21457 | 81.7599 | 15.193 | 22.5 | -119.4529
June | 5 | 291.15 | 70 | 294.261 | 84 | 302.0389 | 1.1546 | 1.0071 | 1.8556e-05 | 1.6095e-05 | 0.026451 | 2.2802e-05 | 0.70671 | 698969.9633 | Turbulent | 785.5792 | 9.2352 | HOT | 0.23195 | 9.2352 | 0.03655 | 0.19236 | 212.8279 | 16.9475 | 22.5 | -252.2754
July | 5 | 291.15 | 70 | 294.261 | 88 | 304.2611 | 1.1472 | 1.0072 | 1.8661e-05 | 1.6319e-05 | 0.026615 | 2.3131e-05 | 0.7064 | 689394.5114 | Turbulent | 768.3306 | 9.0886 | HOT | 0.24097 | 9.0886 | 0.03542 | 0.18639 | 282.36 | 17.4898 | 22.5 | -322.3498
August | 5 | 291.15 | 70 | 294.261 | 86 | 303.15 | 1.1509 | 1.0071 | 1.8609e-05 | 1.6207e-05 | 0.026533 | 2.2966e-05 | 0.70656 | 694149.2168 | Turbulent | 776.9011 | 9.1616 | HOT | 0.2367 | 9.1616 | 0.035943 | 0.18916 | 247.3349 | 17.2342 | 22.5 | -287.0691
September | 5 | 291.15 | 70 | 294.261 | 79 | 299.2611 | 1.1648 | 1.007 | 1.8423e-05 | 1.5824e-05 | 0.026241 | 2.2402e-05 | 0.70719 | 710934.6667 | Turbulent | 807.1067 | 9.413 | HOT | 0.21676 | 9.413 | 0.038674 | 0.20352 | 129.3159 | 16.0181 | 22.5 | -167.834
October | 5 | 291.15 | 70 | 294.261 | 68 | 293.15 | 1.1934 | 1.0069 | 1.8117e-05 | 1.528e-05 | 0.025752 | 2.1596e-05 | 0.70878 | 736239.6804 | Turbulent | 852.6655 | 9.759 | COLD | 0.17178 | 9.759 | 0.047192 | 0.24812 | 23.5211 | 13.1389 | 22.5 | 14.16
November | 6 | 291.15 | 70 | 294.261 | 57 | 287.0389 | 1.2219 | 1.0067 | 1.7812e-05 | 1.4736e-05 | 0.025263 | 2.0789e-05 | 0.71037 | 916095.1125 | Turbulent | 1164.8345 | 13.0788 | COLD | 0.23009 | 13.0788 | 0.036589 | 0.19364 | 197.3568 | 16.8351 | 22.5 | 191.6919
December | 6 | 291.15 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888 | COLD | 0.25358 | 13.4888 | 0.033727 | 0.17877 | 395.2987 | 18.2359 | 22.5 | 391.0346
[5 empty] | Table A4 Data | 250 | 1.3947 | 1.006 | 1.596e-05 | 1.144e-05 | 0.0223 | 1.59e-05 | 0.72
[6 empty] | 300 | 1.1614 | 1.007 | 1.846e-05 | 1.589e-05 | 0.0263 | 2.25e-05 | 0.707
[6 empty] | 350 | 0.995 | 1.009 | 2.082e-05 | 2.092e-05 | 0.03 | 2.99e-05 | 0.7

## Required_6 (WRONG) (hidden)
h_IN | 0.25358 | W/m2K
h_OUT | 13.4888 | W/m2K
T_air | 280.9278 | K
[7 empty] | 0.085729 |  | 0.02722 |  | 0.0016116
|  |  | 0.14084 |  | 0.013192 | [7 empty] | 280.9278 | K
[7 empty] | 10.5161 |  | 0.056154 |  | 0.19769
|  |  | 0.15774 |  | 0.032771 |  | 0.0029654
|  |  | 0.12721 |  | 0.035217 |  | 0.0023915
294.26 | K |  | 0.17925 |  | 0.03371 |  | 0.0033698 |  | 280.9278 | K
|  |  | 0.14084 |  | 0.035528 |  | 0.0026477
|  |  | 0.21909 |  | 0.035533 |  | 0.0041186
[7 empty] | 0.045855 |  | 0.0355
|  |  | 0.11267 |  | 0.013192 | [5 empty] | 291 | K
[7 empty] | 0.11267 |  | 0.04151
|  |  | 0.15403 |  | 0.11336 |  | 280.9278 | K
0.19348
0.16482
294.26 | K |  | 0.21633 |  | 280.9278 | K
0.17902
0.25874
|  |  | 0.12586 |  | 0.053255 |  | 291 | K
|  |  | 0.26739 |  | 280.9278 | K
294.26 | K |  | 0.039511 |  | 280.9278 | K
|  |  | 0.17912 |  | 291 | K
294.26 | K |  | 0.034424 |  | 280.9278 | K |  | 387.2903 | W
294.26 | K |  | 0.17912 |  | 291 | K |  | 18.2001 | W
|  |  |  | q_Home | 387.2903
|  |  |  | q_Soil | 18.2001
|  |  |  | R_Home | 0.034424
|  |  |  | R_Soil | 0.17912

## Required_6_Plot (WRONG) (hidden)
| Wind Speed (m/s) | Soil Temp (K) | Home Temp (F) | Home Temp (K) | Air Temp (F) | Air Temp (K) | Density (kg/m3) | Cp (KJ/kgK) | Dynamic Visocity (Ns/m2) | Kinematic Viscosity (m2/s) | Thermal Conductivity (W/mK) | Thermal Diffusivity (m2/s) | Prandlts Number | Reynolds Number | Rayleigh Number | Nusselt Number | Heat Transfer Coefficient Outside (W/m2K) | Month | h_IN (W/m2K) | h_OUT (W/m2K) | R_Home (K/W) | R_Soil (K/W) | q_Home (W) | q_Soil (W) | q_5Human,2Cat (W) | q_Required (W)
January | 6 | 291.15 | 70 | 294.261 | 42 | 278.7056 | 1.2608 | 1.0066 | 1.7395e-05 | 1.3995e-05 | 0.024596 | 1.9689e-05 | 0.71254 | 964644.3936 | Turbulent | 1248.0078 | 13.6429 | COLD | 0.25993 | 13.6429 | 0.033736 | 0.17556 | 461.057 | 18.5696 | 22.5 | 457.1266
February | 6 | 291.15 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888 | COLD | 0.25358 | 13.4888 | 0.034424 | 0.17912 | 387.2903 | 18.2001 | 22.5 | 382.9904
March | 7 | 291.15 | 70 | 294.261 | 55 | 285.9278 | 1.2271 | 1.0067 | 1.7756e-05 | 1.4638e-05 | 0.025174 | 2.0642e-05 | 0.71066 | 1075998.1069 | Turbulent | 1431.7755 | 16.0195 | COLD | 0.23544 | 16.0195 | 0.036499 | 0.19035 | 228.2881 | 17.1265 | 22.5 | 222.9146
April | 6 | 291.15 | 70 | 294.261 | 66 | 292.0389 | 1.1985 | 1.0068 | 1.8062e-05 | 1.5181e-05 | 0.025663 | 2.1449e-05 | 0.70907 | 889242.4715 | Turbulent | 1118.4771 | 12.7572 | COLD | 0.19138 | 12.7572 | 0.043522 | 0.22647 | 51.0345 | 14.3951 | 22.5 | 42.9296
May | 5 | 291.15 | 70 | 294.261 | 76 | 297.5944 | 1.1726 | 1.007 | 1.834e-05 | 1.5676e-05 | 0.026108 | 2.2182e-05 | 0.70763 | 717661.8895 | Turbulent | 819.2468 | 9.506 | HOT | 0.20356 | 9.506 | 0.041484 | 0.21492 | 80.379 | 15.1682 | 22.5 | -118.0472
June | 5 | 291.15 | 70 | 294.261 | 84 | 302.0389 | 1.1546 | 1.0071 | 1.8556e-05 | 1.6095e-05 | 0.026451 | 2.2802e-05 | 0.70671 | 698969.9633 | Turbulent | 785.5792 | 9.2352 | HOT | 0.23195 | 9.2352 | 0.037249 | 0.19271 | 208.837 | 16.9166 | 22.5 | -248.2535
July | 5 | 291.15 | 70 | 294.261 | 88 | 304.2611 | 1.1472 | 1.0072 | 1.8661e-05 | 1.6319e-05 | 0.026615 | 2.3131e-05 | 0.7064 | 689394.5114 | Turbulent | 768.3306 | 9.0886 | HOT | 0.24097 | 9.0886 | 0.036118 | 0.18675 | 276.9047 | 17.4569 | 22.5 | -316.8616
August | 5 | 291.15 | 70 | 294.261 | 86 | 303.15 | 1.1509 | 1.0071 | 1.8609e-05 | 1.6207e-05 | 0.026533 | 2.2966e-05 | 0.70656 | 694149.2168 | Turbulent | 776.9011 | 9.1616 | HOT | 0.2367 | 9.1616 | 0.036641 | 0.18951 | 242.6224 | 17.2023 | 22.5 | -282.3246
September | 5 | 291.15 | 70 | 294.261 | 79 | 299.2611 | 1.1648 | 1.007 | 1.8423e-05 | 1.5824e-05 | 0.026241 | 2.2402e-05 | 0.70719 | 710934.6667 | Turbulent | 807.1067 | 9.413 | HOT | 0.21676 | 9.413 | 0.039373 | 0.20387 | 127.0181 | 15.9905 | 22.5 | -165.5086
October | 5 | 291.15 | 70 | 294.261 | 68 | 293.15 | 1.1934 | 1.0069 | 1.8117e-05 | 1.528e-05 | 0.025752 | 2.1596e-05 | 0.70878 | 736239.6804 | Turbulent | 852.6655 | 9.759 | COLD | 0.17178 | 9.759 | 0.047895 | 0.24847 | 23.1758 | 13.1203 | 22.5 | 13.7961
November | 6 | 291.15 | 70 | 294.261 | 57 | 287.0389 | 1.2219 | 1.0067 | 1.7812e-05 | 1.4736e-05 | 0.025263 | 2.0789e-05 | 0.71037 | 916095.1125 | Turbulent | 1164.8345 | 13.0788 | COLD | 0.23009 | 13.0788 | 0.037288 | 0.19399 | 193.657 | 16.8046 | 22.5 | 187.9617
December | 6 | 291.15 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888 | COLD | 0.25358 | 13.4888 | 0.034424 | 0.17912 | 387.2903 | 18.2001 | 22.5 | 382.9904
[5 empty] | Table A4 Data | 250 | 1.3947 | 1.006 | 1.596e-05 | 1.144e-05 | 0.0223 | 1.59e-05 | 0.72
[6 empty] | 300 | 1.1614 | 1.007 | 1.846e-05 | 1.589e-05 | 0.0263 | 2.25e-05 | 0.707
[6 empty] | 350 | 0.995 | 1.009 | 2.082e-05 | 2.092e-05 | 0.03 | 2.99e-05 | 0.7

## Required_6_Model
h_IN | 0.25358 | W/m2K
h_OUT | 13.4888 | W/m2K
T_air | 280.9278 | K
[7 empty] | 0.085729 |  | 0.02623 | 0.018741 | 0.0016116
|  |  | 0.14084 | 0.012841 | 0.030788 | [7 empty] | 280.9278 | K
[7 empty] | 10.5161 |  | 0.05018 | 2.2989 | 0.19769
|  |  | 0.15774 | 0.02881 | 0.034483 |  | 0.0029654
|  |  | 0.12721 | 0.02977 | 0.027809 |  | 0.0023915
294.26 | K |  | 0.17925 | 0.0301 | 0.039185 |  | 0.0033698 |  | 280.9278 | K
|  |  | 0.14084 | 0.03033 | 0.030788 |  | 0.0026477
|  |  | 0.21909 | 0.03412 | 0.047893 |  | 0.0041186
[7 empty] | 0.045855 |  | 0.0355 | 0.010024
|  |  | 0.11267 | 0.012841 | 0.024631 | [6 empty] | 291 | K
[7 empty] | 0.11267 |  | 0.04151 | 0.024631
|  |  | 0.18447 | 0.13098 |  | 280.9278 | K
0.224
0.18718
294.26 | K |  | 0.25191 | 280.9278 | K
0.20461
0.30522
|  |  | 0.15014 | 0.060475 |  | 291 | K
|  |  | 0.31545 | 280.9278 | K
294.26 | K |  | 0.045578 | 280.9278 | K
|  |  | 0.21062 | 291 | K
294.26 | K |  | 0.039824 | 280.9278 | K |  | 334.7752 | W
294.26 | K |  | 0.21062 | 291 | K |  | 15.4782 | W

## Required_6_Plot
| Wind Speed (m/s) | Soil Temp (K) | Home Temp (F) | Home Temp (K) | Air Temp (F) | Air Temp (K) | Density (kg/m3) | Cp (KJ/kgK) | Dynamic Visocity (Ns/m2) | Kinematic Viscosity (m2/s) | Thermal Conductivity (W/mK) | Thermal Diffusivity (m2/s) | Prandlts Number | Reynolds Number | Rayleigh Number | Nusselt Number | Heat Transfer Coefficient Outside (W/m2K) | Month | h_IN (W/m2K) | h_OUT (W/m2K) | R_Home (K/W) | R_Soil (K/W) | q_Home (W) | q_Soil (W) | q_5Human,2Cat (W) | q_Added_Fiber (W) | q_None_Fiber (W) | Difference (W) | % Change
January | 6 | 291.15 | 70 | 294.261 | 42 | 278.7056 | 1.2608 | 1.0066 | 1.7395e-05 | 1.3995e-05 | 0.024596 | 1.9689e-05 | 0.71254 | 964644.3936 | Turbulent | 1248.0078 | 13.6429 | COLD | 0.25993 | 13.6429 | 0.039137 | 0.20706 | 397.4351 | 15.7444 | 22.5 | 390.6794 | 466.89 | 76.2106 | 16.32%
February | 6 | 291.15 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888 | COLD | 0.25358 | 13.4888 | 0.039824 | 0.21062 | 334.7752 | 15.4782 | 22.5 | 327.7534 | 391.0346 | 63.2812 | 16.18%
March | 7 | 291.15 | 70 | 294.261 | 55 | 285.9278 | 1.2271 | 1.0067 | 1.7756e-05 | 1.4638e-05 | 0.025174 | 2.0642e-05 | 0.71066 | 1075998.1069 | Turbulent | 1431.7755 | 16.0195 | COLD | 0.23544 | 16.0195 | 0.041897 | 0.22184 | 198.8742 | 14.6954 | 22.5 | 191.0696 | 227.4025 | 36.3329 | 15.98%
April | 6 | 291.15 | 70 | 294.261 | 66 | 292.0389 | 1.1985 | 1.0068 | 1.8062e-05 | 1.5181e-05 | 0.025663 | 2.1449e-05 | 0.70907 | 889242.4715 | Turbulent | 1118.4771 | 12.7572 | COLD | 0.19138 | 12.7572 | 0.048916 | 0.25794 | 45.4065 | 12.6388 | 22.5 | 35.5453 | 43.7884 | 8.2431 | 18.82%
May | 5 | 291.15 | 70 | 294.261 | 76 | 297.5944 | 1.1726 | 1.007 | 1.834e-05 | 1.5676e-05 | 0.026108 | 2.2182e-05 | 0.70763 | 717661.8895 | Turbulent | 819.2468 | 9.506 | HOT | 0.20356 | 9.506 | 0.04688 | 0.2464 | 71.1273 | 13.2306 | 22.5 | -106.8579 | -119.4529 | 12.595 | 10.54%
June | 5 | 291.15 | 70 | 294.261 | 84 | 302.0389 | 1.1546 | 1.0071 | 1.8556e-05 | 1.6095e-05 | 0.026451 | 2.2802e-05 | 0.70671 | 698969.9633 | Turbulent | 785.5792 | 9.2352 | HOT | 0.23195 | 9.2352 | 0.042647 | 0.2242 | 182.4006 | 14.5407 | 22.5 | -219.4413 | -252.2754 | 32.8341 | 13.02%
July | 5 | 291.15 | 70 | 294.261 | 88 | 304.2611 | 1.1472 | 1.0072 | 1.8661e-05 | 1.6319e-05 | 0.026615 | 2.3131e-05 | 0.7064 | 689394.5114 | Turbulent | 768.3306 | 9.0886 | HOT | 0.24097 | 9.0886 | 0.041517 | 0.21824 | 240.8918 | 14.9378 | 22.5 | -278.3296 | -322.3498 | 44.0203 | 13.66%
August | 5 | 291.15 | 70 | 294.261 | 86 | 303.15 | 1.1509 | 1.0071 | 1.8609e-05 | 1.6207e-05 | 0.026533 | 2.2966e-05 | 0.70656 | 694149.2168 | Turbulent | 776.9011 | 9.1616 | HOT | 0.2367 | 9.1616 | 0.04204 | 0.221 | 211.4632 | 14.7511 | 22.5 | -248.7143 | -287.0691 | 38.3547 | 13.36%
September | 5 | 291.15 | 70 | 294.261 | 79 | 299.2611 | 1.1648 | 1.007 | 1.8423e-05 | 1.5824e-05 | 0.026241 | 2.2402e-05 | 0.70719 | 710934.6667 | Turbulent | 807.1067 | 9.413 | HOT | 0.21676 | 9.413 | 0.04477 | 0.23535 | 111.7057 | 13.8516 | 22.5 | -148.0573 | -167.834 | 19.7767 | 11.78%
October | 5 | 291.15 | 70 | 294.261 | 68 | 293.15 | 1.1934 | 1.0069 | 1.8117e-05 | 1.528e-05 | 0.025752 | 2.1596e-05 | 0.70878 | 736239.6804 | Turbulent | 852.6655 | 9.759 | COLD | 0.17178 | 9.759 | 0.053288 | 0.27993 | 20.8303 | 11.6458 | 22.5 | 9.9761 | 14.16 | 4.1839 | 29.55%
November | 6 | 291.15 | 70 | 294.261 | 57 | 287.0389 | 1.2219 | 1.0067 | 1.7812e-05 | 1.4736e-05 | 0.025263 | 2.0789e-05 | 0.71037 | 916095.1125 | Turbulent | 1164.8345 | 13.0788 | COLD | 0.23009 | 13.0788 | 0.042686 | 0.22548 | 169.1677 | 14.4579 | 22.5 | 161.1256 | 191.6919 | 30.5663 | 15.95%
December | 6 | 291.15 | 70 | 294.261 | 46 | 280.9278 | 1.2504 | 1.0066 | 1.7506e-05 | 1.4193e-05 | 0.024774 | 1.9982e-05 | 0.71196 | 951201.7828 | Turbulent | 1225.0589 | 13.4888 | COLD | 0.25358 | 13.4888 | 0.039824 | 0.21062 | 334.7752 | 15.4782 | 22.5 | 327.7534 | 391.0346 | 63.2812 | 16.18%
[5 empty] | Table A4 Data | 250 | 1.3947 | 1.006 | 1.596e-05 | 1.144e-05 | 0.0223 | 1.59e-05 | 0.72
[6 empty] | 300 | 1.1614 | 1.007 | 1.846e-05 | 1.589e-05 | 0.0263 | 2.25e-05 | 0.707
[6 empty] | 350 | 0.995 | 1.009 | 2.082e-05 | 2.092e-05 | 0.03 | 2.99e-05 | 0.7

## Sheet2 (hidden)
| January | February | March | April | May | June | July | August | September | October | November | December
h_IN | 0.25993 | 0.25358 | 0.23544 | 0.19138 | 0.20356 | 0.23195 | 0.24097 | 0.2367 | 0.21676 | 0.17178 | 0.23009 | 0.25358
h_OUT | 13.6429 | 13.4888 | 16.0195 | 12.7572 | 9.506 | 9.2352 | 9.0886 | 9.1616 | 9.413 | 9.759 | 13.0788 | 13.4888
T_air | 278.7056 | 280.9278 | 285.9278 | 292.0389 | 297.5944 | 302.0389 | 304.2611 | 303.15 | 299.2611 | 293.15 | 287.0389 | 280.9278
q_Home | 397.4351 | 334.7752 | 198.8742 | 45.4065 | 71.1273 | 182.4006 | 240.8918 | 211.4632 | 111.7057 | 20.8303 | 169.1677 | 334.7752
q_Soil | 15.7444 | 15.4782 | 14.6954 | 12.6388 | 13.2306 | 14.5407 | 14.9378 | 14.7511 | 13.8516 | 11.6458 | 14.4579 | 15.4782
R_Home | 0.039137 | 0.039824 | 0.041897 | 0.048916 | 0.04688 | 0.042647 | 0.041517 | 0.04204 | 0.04477 | 0.053288 | 0.042686 | 0.039824
R_Soil | 0.20706 | 0.21062 | 0.22184 | 0.25794 | 0.2464 | 0.2242 | 0.21824 | 0.221 | 0.23535 | 0.27993 | 0.22548 | 0.21062
q_Home | 461.057 | 387.2903 | 228.2881 | 51.0345 | 80.379 | 208.837 | 276.9047 | 242.6224 | 127.0181 | 23.1758 | 193.657 | 387.2903
q_Soil | 18.5696 | 18.2001 | 17.1265 | 14.3951 | 15.1682 | 16.9166 | 17.4569 | 17.2023 | 15.9905 | 13.1203 | 16.8046 | 18.2001
R_Home | 0.033736 | 0.034424 | 0.036499 | 0.043522 | 0.041484 | 0.037249 | 0.036118 | 0.036641 | 0.039373 | 0.047895 | 0.037288 | 0.034424
R_Soil | 0.17556 | 0.17912 | 0.19035 | 0.22647 | 0.21492 | 0.19271 | 0.18675 | 0.18951 | 0.20387 | 0.24847 | 0.19399 | 0.17912
q_Home | 470.7832 | 395.2987 | 232.7443 | 51.871 | 81.7599 | 212.8279 | 282.36 | 247.3349 | 129.3159 | 23.5211 | 197.3568 | 395.2987
q_Soil | 18.6068 | 18.2359 | 17.1582 | 14.4174 | 15.193 | 16.9475 | 17.4898 | 17.2342 | 16.0181 | 13.1389 | 16.8351 | 18.2359
R_Home | 0.03304 | 0.033727 | 0.0358 | 0.04282 | 0.040783 | 0.03655 | 0.03542 | 0.035943 | 0.038674 | 0.047192 | 0.036589 | 0.033727
R_Soil | 0.1752 | 0.17877 | 0.19 | 0.22612 | 0.21457 | 0.19236 | 0.18639 | 0.18916 | 0.20352 | 0.24812 | 0.19364 | 0.17877